## Sheet 1
Automatic fire alarm system
Note: External cables are processed in the external infrastructure section
RB | Description of technical requirements | Manufacturer | Model
1 | Microprocessor fully redundant control panel, based on communication with intelligent fire detectors and other elements via loops with a capacity of at least 128 addresses per loop, which in the basic configuration contains: a) metal cabinet, with an opening for the internal control panel; b) motherboard with main processor; c) power supply unit, with battery charger; d) rack with slots for up to 11 modules; e) space for 2 batteries 12V/45Ah for operation without mains power supply, complete with two batteries of the specified capacity; NOTE: the required total capacity is around 60Ah, so additional batteries in a separate position are foreseen;f) motherboard B5-MCUA, which, along with the control panel, contains a connector for connecting the internal control panel; g) B8-BAF module for connecting external control panels; h) slot for memory SD card; i) USB interface for PC connection; j) LAN interface; k) 3 monitored galvanically isolated inputs; l) 2 monitored outputs; m) 3 programmable relay outputs (300W/2500VA); n) Event memory (up to 10,000); o) B8-PSU power supply unit equipped with electronic fuses; p) input voltage 110 VAC -15% to 230 VAC +10%, 47-63Hz; q) output voltage 26.3 Vdc (+50°C) to 28.3 Vdc (0°C), output current 7A, outputs for external consumers 5 x 27Vdc;
r) Dimensions of the control unit 600x445x225 (HxWxD), steel casing red color RAL 3000, IP protection IP30, operating temperature from -5° to +50°C, weight 15Kg (without batteries). s) The control unit is manufactured in accordance with EN 54-2, EN 54-4, DIN EN 12094-1 and has the VdS 2496 certificate; t) Loop module. The module is connected to a slot in the central office, 2 loops for connecting address elements, up to 250 address elements in each loop, up to 3500m length of each loop, possibility of two-zone and two-detector dependence, possibility of switching off any detector, permanent monitoring of all elements in the loop, localization of interruptions and short circuit, consumption 35mA. u) Relay module with 16 programmable 24V/3A relay contacts v) Module for telephone/SMS notification of alarm conditions
4 | Addressable interactive multi-sensor optical-thermal fire detector complete with appropriate base. THE DETECTOR IS CONFIGURED AS OPTICAL, and has the following characteristics: a) it can be configured as an optical detector, a thermal detector or a combined optical-thermal detector in accordance with EN 54-7, EN 54-5 and EN54-17 standards, for the early detection of smoldering and open fires with or without smoke; b) the optical part of the detector has automatic adaptation to the state of the environment in which it is located (automatic adjustment/adjustment of sensitivity depending on the ambient temperature); c) the detector has the possibility of programming the alarm threshold and permanent monitoring only for the purpose of automatic interactive adaptation; d) contains an integrated loop isolator; e) programmatic address assignment and automatic recognition of the detector's unique serial number; f) working temperature -25°/+60°C; g) degree of protection IP 44 (with base), housing made of ABS plastic; h) the base has the possibility of securing against unauthorized removal of the detector. i) dimensions 118.8x58.1mm, color RAL 9003
5 | Addressable interactive multi-sensor optical-thermal fire detector complete with appropriate base. THE DETECTOR IS CONFIGURED AS COMBINED, and has the following characteristics: a) it can be configured as an optical detector, thermal detector or combined optical-thermal detector in accordance with EN 54-7, EN 54-5 and EN54-17 standards, for the early detection of smoldering and open fires with or without smoke; b) the optical part of the detector has automatic adaptation to the state of the environment in which it is located (automatic adjustment/adjustment of sensitivity depending on the ambient temperature); c) the detector has the possibility of programming the alarm threshold and permanent monitoring only for the purpose of automatic interactive adaptation; d) contains an integrated loop isolator; e) programmatic address assignment and automatic recognition of the detector's unique serial number; f) working temperature -25°/+60°C; g) degree of protection IP 44 (with base), housing made of ABS plastic; h) the base has the possibility of securing against unauthorized removal of the detector. i) dimensions 118.8x58.1mm, color RAL 9003
6 | Addressable interactive optical detector in a protective housing for fire detection in ventilation ducts, single-tube air sampling system, a) application in ventilation ducts in which the air speed is 1-20 m/s, b) flow indicator, c) simple installation, d) contains air sampling pipe for mounting on the housing containing the addressable interactive optical fire detector for fire detection in ventilation ducts with a width of 0.15-1m e) Degree of protection IP54 f) operating temperature from -25° to +60°C
7 | Procurement, delivery, installation and connection of an addressable manual fire detector for operation in an addressable loop with the following characteristics: a) in accordance with EN54-11 and EN54-17 standards; b) the caller should have: the so-called "double action" activation (glass break + button press); c) LED alarm indication; d) integrated loop isolator; e) degree of protection min. IP52; f) working temperature -20°/+50°C; d) red color