## Sheet1
POSITION FROM PRE-MEASUREMENT | DESCRIPTION FROM MEASUREMENTS | MANUFACTURER | MODEL
III.3 | Procurement and installation of polyethylene water pipes for a working pressure of 10 bar (SDR 17). Sleeves for the transition to metal (LG and initial pipes) shaped pieces are not included in the price. It is calculated and paid per meter of installed and tested water pipes.
III.1 | Carry out procurement and installation of polypropylene water pipes with all appropriate fittings, flow and discharge valves and thermal insulation. The pipes must have a certificate that they can be used as pipes for transporting drinking water. Wall pipes must be fixed with double clamps every 1.5-2.0m. During assembly, it is necessary to follow the manufacturer's recommendations, especially in relation to temperature expansion, both in free space (lyres and axial compensators) and in walls (wrapping pipes with felt, etc.). The entire plumbing installation must be tested to a pressure of 12 bar according to current regulations before closing the grooves and plastering. It is calculated and paid per meter of installed water pipe, including leak valves, discharge elements for PP-R pipes and thermal insulation.
III.2 | Supply and install galvanized steel water pipes with all appropriate fittings. Pipes must comply with current regulations. Pipes to the walls must be fixed with double clamps every 1.5-2.0m. Pipes in the ground and through the structure must be coated once with bitumen, then with bitumen and wrapped with bituminized jute. (The water supply connection can also be made of polypropylene water pipes - hose diameter Dn 90x5.4 - inner diameter 79.2 mm.) It is calculated and paid per meter of installed water pipe.
II.2 | Procurement and installation of plastic pipes for laying in the ground, which correspond to valid standards. In all places determined by the project, install appropriate fashion and revision pieces. Before backfilling, test the entire sewage network for water resistance in the presence of the supervisory authority. It is calculated and paid per meter of installed and tested network, measured along the axis of pipes and shaped pieces.
II.1 | Carry out procurement and installation of plastic sewage pipes that are installed in the building above the ground. Fasten the pipes under each muff with iron ram-shells. Hang the pipe from the ceiling around each sleeve with a 3/40mm flat iron stirrup. all necessary trimming and piercing of brick and concrete walls are not paid for separately, but are included in the price of the required meter of pipe. Until their installation, close the unfinished parts of the network, connections for verticals or sanitary facilities with temporary wooden plugs of the appropriate diameter. It is processed and paid for per m' of moated and tested mesh, measured along the axis of pipes and shaped pieces.
IV.1 IV.2 IV.4 IV.5 IV.12 IV.18 IV.20 IV.21 | A. English toilet - cantilever, set - for convicts - cantilever toilet bowl - toilet seat with full plastic lid, equipped with buffers - low-mounted flush, built-in flush type, connected to the bowl by a Ø32mm plastic pipe with a clamp and a rubber buffer. Activating flushing via the hydraulic button. B. English toilet - monobloc, set - for staff - standing toilet made of white faience - toilet seat with full plastic lid, equipped with bumpers - low-mounted flush, monobloc type, connected to the bowl by a Ø32mm plastic pipe with a clamp and a rubber bumper. Activating flushing with the classic button on the top. C. Washbasin for convicts with siphon D. Washbasin for staff with siphon E. Shower tub 80x80cm with drain F. One-piece sink with siphon G. Trocadero with grate and high-mounted flusher H. Enamelled steel tap with back
IV.17 | Floor drain Ø50 - vertical with dry siphon type HL Primus, or similar. Ø50 - horizontal with dry siphon type HL Primus, or similar. Ø50 - through in the direction Ø50 - through at an angle Ø100 - vertical with dry siphon and nickel grating Ø100 - vertical with dry siphon and LG grating (in technical rooms)
IV.6 IV.7 IV.13 IV.16 IV.19 IV.20IV.22 | A. Faucet for the sink - standing B. Faucet for the sink (for convicts) - standing C. Faucet for the shower D. Shower head - wall-mounted E. Faucet for the sink - standing, two connections F. Faucet for the trocadero G. Hollander faucet for enamelled steel tap with back
V.1 | Hydro-stations for the hydrant network: Membrane vessel under pressure with a volume of 18 liters. The hydrostation is equipped with one electric pump, one diesel pump and a pilot pump to maintain pressure in the network, as well as two electric control panels and automatics that are paired with each other and supplied by the pump manufacturer. Q=5.0 l/s, H=25.0m.
V.2 | Hydro-stations for drinking water: Membrane vessel under pressure with a volume of 24 liters. The hydrostation is equipped with three electric pumps (two working and one spare), as well as with an electric control panel and automation supplied by the pump manufacturer. Q=7.4 l/s, H=17.0m.