## 1-SKS (hidden)
1 | Structured cable network
RB | Description of technical requirements | Manufacturer | Model
1.1 | Server free-standing rack cabinet with the following minimum characteristics: Dimensions: 47U, 800x1000 Construction: a.1) The cabinet is with perforated front and back doors a.2) Door perforation must be at least 80% a.3) It must have removable sides, works for easier access to equipment a.4) Sides should be equipped with a locking latch a.5) Equipped with four 19" vertical supports, with the option of depth adjustment and double unit marking (U) a.6) Provided 19" cable entries on the upper and lower plates a.7) Equipped with 2 cable entries with brushes, 1U a.8) Equipped with a fixed base made of solid plates with a minimum height of 100mm. Load capacity: b.1) Minimum 15kg per unit Mechanical characteristics: c.1) With IP20 degree of protection in accordance with IEC EN 60529 c.2) With IK08 degree of protection in accordance with standard IEC EN 62262 c.3) Resistance to shocks and vibrations in accordance with standard IEC 61587-1, level DL4 c.4) Corrosion resistance: Class C2 in accordance with EN ISO 12944-2 and 3K3 in accordance with IEC EN 60721-3-3 Compliance with directives: d. 1) In compliance with standards EIC 60950-1, ANSI/EIA-310-E and IEC 60297-3-100 Compatibility: e.1) All racks and accompanying equipment (fans, thermostat, shelves, etc.) must be the same manufacturer in order to achieve full equipment compatibility
1.2 | Modular panel equipped with 24 modules at an angle for horizontal cabling with the following minimum characteristics: Panel characteristics: a.1) 1U, for installation of 24 modules facing both sides at an angle of 30° a.2) Robust steel construction a.3) Equipped with a set for grounding a.4) Equipped with a cable guide a.5) Minimum IP20 degree of protection against water and dust a.6) Operating temperature in the minimum range from -40°C to +70° C a.7) Compliance with the RoHS directive Module characteristics : b.1) Modules are shielded Cat6a b.2) Housing is shielded, made of zinc alloy b.3) Compliant for PoE/PoE+ applications b.4) Keystone bracket, for tool-free installation b.5) For wire diameter AWG 22 to AWG 24 b.6) Insulation resistance minimum 500 MΩ b.7) Fully compliant with European standards ISO/IEC 11801, EN 50173-1 and TIA/EIA 568-C.2 b.8) Compliance with RoHS directive b. .9) Provide a certificate from an independent laboratory proving compliance with the IEC 60603-7 standard Compatibility: c.1) All passive network equipment (optical and copper cables, modules, patch panels, patch cables and optical panels) must be from the same manufacturer
1.3 | Optical distribution panel with the following minimum characteristics:a) Height 1HU, for placement in a 19" cabinet b) With 12 LC OM3 duplex adapters c) With a telescopic pull-out shelf with an inclination of 15° d) IP20 protection in accordance with EN 60529 e) With 24 LC pigtails OM3 f ) Equipped with splice cassettes, holders, heat-shrink protection, and other supporting equipment
1.4 | Optical distribution panel with the following characteristics: a) Height 1HU, for placement in a 19" cabinet b) With 12 SC/APC SM duplex adapters c) With a shelf for telescopic pull-out floor with a slope of 15° d) IP20 protection in accordance with EN 60529 e) With 24 SC/APC of SM pigtails f) Equipped with splice cassettes, holders, heat-shrinkable protections, and other supporting equipment
1.16 | Copper cable Cat6a with the following minimum characteristics: a) The cable is S/FTP Cat7 b) Suitable for PoE / PoE+ applications c) The cable jacket is without halogen elements in accordance with standards 60332-3 d) Smoke emission in accordance with IEC 61034 standard e) CPR certified for use in construction: class minimum B2ca-s1,d1,a1 f) Provide a certificate from an independent laboratory as proof of compliance with the mentioned standard g) The cable complies with the standards: ISO/IEC 11801, EN 50173 and EN 50288 h) Maximum tensile force: 100N i) Operating temperature in the minimum range from -20°C to + 60°C j) Compliance with the RoHS Directive k) All passive network equipment (optical and copper cables, modules, patch panels patch cables and optical panels) must be from the same manufacturer
1.17 | Delivery and laying of optical singlemode cable with 12 fibers with the following characteristics: a) Maximum cable diameter 8.5mm b) With LSOH jacket for outdoor/indoor mounting and rodent protection in the form of glass aramid fibers. c) The cable must satisfy a pulling force of 3000N in accordance with IEC 60794-1-2 E1 d) The required crushing resistance is 8000 N/dm in accordance with IEC 60794-1-2-E3 e) The cable must withstand 5000 cycles bending around a roller of radius 50mm, in accordance with IEC 60794-1-2 E6

## 2-Active (hidden)
2 | Active network equipment
RB | Description of technical requirements | Manufacturer | Model
2.1 | Central modular switch with the following minimum characteristics:
The height of the device must be a maximum of 1 RU - The device must have redundant AC power supplies with a maximum individual power of up to 350W - At least 32 x 100/1000 Mbps Ethernet SFP ports - At least 4 x 10Gbps SFP+ ports - At least 2 x 40Gbps QSFP+ ports - Option expansion by adding modules that would provide additional 2h 40Gbps QSFP+ ports or additional 8h 1/10Gbps SFP/SFP+ ports - At least 3GBRAM memory - At least 4GB flash memory - At least 340Mpps packet forwarding speed - At least 230Gbps switching capacity (460Gbps bidirectional) - Support for stacking (up to 10 switches that would together constitute one logical switch) via standard 10GbE SFP+ or 40GbE QSFP+ interfaces - Support for at least 16 aggregated interfaces (802.3ad LACP LAG – Link Aggregation Group) and at least 16 ports per LAG interface - Support for at least 64,000 entries in the MAC table - Support for at least 64,000 entries in the ARP table - Support for at least 16,000 IPv4 prefixes in the routing table - Support for at least 8,000 IPv4 multicast groups in the routing table - Support for: LACP, 802.1w, 802.1s, MDIX, RADIUS and TACACS+, Storm control, MLD snooping, 802.3x, SNMP, 802.1X, L2-L4 ACL (Access Control List) - Support for: OSPFv4/v6, PIM-SM/SSM/DM, IGMP v1/v2/v3, VRF -Lite - Possibility of support for BGP and IS-IS - Support for jumbo frames of minimum size 9200 bytes - Operating temperature must support the range 0 to 45°C - The device must be delivered with all necessary licenses for the required performance and functionality.
2.2 | switch of the following minimum characteristics:
1U height Minimum 48 x 10/100/1000BASE-T Ethernet RJ-45 PoE+ ports Minimum 4x 1/10G SFP/SFP+ ports PoE+ support on all Ethernet ports Minimum 750W PoE power budget. Bandwidth of at least 88 Gbps unidirectional (or 176 Gbps bidirectional) Bandwidth of at least 130 Mpps RJ-45 Ethernet management interface, USB mini and RJ-45 console port Support for at least 512 IPv4/IPv6 prefixes. Support for a minimum of 2,000 IPv4 and 1,000 IPv6 multicast groups/routes. Support for a minimum of 16,000 MAC addresses Support for a minimum of 1,500 ARP entries Support for a minimum of 4,000 VLANs Support for Jumbo frame size 9216 B Protocol support:, IEEE 802.3ad support (LACP) Support for 802.1X All necessary licenses must be included and delivered with the device Manufacturer's support for at least 3 years (warranty, support, service support) Included in the price are 4x 1G multimode SFP modules from the same manufacturer as the switch
2.3 | Software for monitoring and analyzing network resources with the following features: The software should monitor low power systems. The software should alert users when a problem occurs and be alerted again when the problem is resolved via email or SMS. The software should monitor via network services (SMTP, POP3, HTTP, NNTP, ICMP, SNMP, FTP, SSH) Software should monitor low current system resources (CPU load, disk usage, system logs) on most network operating systems, including Microsoft Windows, using monitoring agents. The software should monitor any hardware (eg temperature probes, alarms, etc. ) The software should enable remote monitoring supported via SSH or SSL encrypted tunnels. Web-interface for viewing current network status, notifications, problem history, log files, etc.

## 4-Speech communications
4 | Voice communication system
RB | Description of technical requirements | Manufacturer | Model
4.1 | IP audio management system software provides the following minimum features: a) Centralized administration and control from one location for up to 5000 devices in the system and up to 100 zones b) Centralized control and settings of audio devices from one location c) Graphical interface for controlling settings d) Creation zone and assigning belonging to certain zones (zone management) e) Playing different contents (voice announcements, background music, etc.) in different zones and at different times f) Flexible planning of voice announcements and other audio content at a predefined time g) Playing voice announcements or emergency notifications in real time by different zones h) Intuitive graphic interface i) Necessary support for audio file formats: mp3, mp4, mpeg, aac, wma, ogg, flac, wav j) Support for two-way communication via SIP protocol to connect to SIP telephone exchange via SIP trunk or peer-to-peer k) Support for VoIP codecs: L16 mono, G.722, G.711u, G.711a l) Support for network protocols: IPv4, HTTP, HTTPS, DNS, NTP, RTP, RTSP, TCP, UDP, DHCP, SIP, mDNS, M3U
Warranty and service support:n) Minimum 3-year manufacturer's warranty
4.2 | Multifunctional IP voice communications console with the following minimum features: a) With a color LCD touch screen, minimum 15" b) Intuitive interface for selecting functions on the screen c) Equipped with two headphones d) Equipped with a gooseneck microphone e) Making a minimum of 32 simultaneous calls f) Support for the SIP signaling protocol for integration with IP/SIP telephone exchange g) Call control on the touch screen (Mute, hold, Transfer function, Conferences, etc.) h) Equipped with a minimum of 8 USB ports for connecting external peripheral equipment (web camera, additional headphones, keyboard, mouse or fig.) i) Internal directory for a minimum of 10,000 contacts, of which a minimum of 140 are visible simultaneously on the screen j) A minimum of one year of manufacturer service support
4.3 | A high class SIP phone with the following minimum features:a) Minimum 5 programmable line keys b) Backlit color screen - WVGA minimum resolution 800×480 c) Minimum 2 10/100/1000BASE-T RJ45 ports - two-port Ethernet switch d) Support for Wi-fi, IEEE 802.11a , 802.11b, 802.11g, 802.11n, and 802.11ac standards e) IEEE 802.11e, Wi-Fi Multimedia (WMM) f) Button with LED indication of voice messages waiting g) Volume buttons h) Mute and Hold dedicated keys i) Built-in full-duplex speakerphone j) Support for PoE power supply - IEEE 802.3af and 802.3at k) Support for telephone functions: call identification, call forwarding and redirection, 3-way conference connection, call parking, music on hold, call waiting l) Call history list m) SIP signaling protocol support on Speech codecs: G.711 a-law and mu-law, G.722, G.729a/b, iLBC, iSAC, G.722.1, G. 772.2, OPUS
4.4 | An IP phone with the following minimum features:a) 4-line telephone, with support for adding modules with additional keys b) LCD graphic screen with backlight (396 x 162 pixels) c) 2 x 10/100T RJ45 ports - two-port Ethernet switch d) Key with LED indication of voice messages on hold e) Volume keys f) Mute, Hold and Conference key g) Built-in full-duplex speakerphone h) Support for PoE power supply (IEEE 802.3.af) i) Support for telephone functions: call identification, forwarding and redirection calls, 3-way conference connection, call parking, music on hold, call on hold j) Call history list k) Support for SIP signaling protocol l) Support for SIP in NAT networks - including STUN m) Speech codecs: G.711 ( A-law and m-law), G.722.2, G.722, G.729 (a, b, ab), ILBC, iSAC, OPU
4.5 | An expansion console with the following minimum features:a) Minimum of 14 programmable LED keys b) LED in different colors (green, red and orange) c) Supports call forwarding, call forwarding, direct calling d) Two 3.5-in (9-cm) grayscale backlit LCD displays, resolution 160 x 270 e) Power supply from the IP telephone to which it is connected f) Fully compatible with IP telephones in position 4.4
4.6 | Delivery, assembly, adjustment, programming, testing and commissioning of the control unit of the IP intercom module for installation in the technical duct between the cells with the following minimum characteristics:a) LAN interface: 2x RJ45 10/100T ports (auto-MDIX), Integrated 2-port LAN switch b) Power supply: PoE 802.3af (class 0 to 12.95W) or external power supply 9 to 36 V ± 10 % / 2 A DC c) Integrated 10W amplifier for an external speaker d) Interfaces for connecting an external microphone e) Two programmable active outputs - output current 600mA, with overvoltage and short circuit protection f) Possibility of connecting external visual indicators, with programmable activation duration g ) Two programmable, galvanically isolated inputs h) Minimum of three outputs for connecting programmable LED indicators i) Interface for connecting a matrix keyboard 4x4 or up to 16 independent external ones j) Multifunctional RESET button k) Realization of two-way communication l) Echo suppression - Acoustic Echo cancellation (AEC ) m) Supported protocols: SIP 2.0, IPv4, ARP, TCP, UDP, DHCP n) Audio streaming (RTP, RTSP) o) Time synchronization (SNTP), p) Automatic configuration and firmware upgrade: TFTP r) Configuration via web: HTTP/HTTPS s) The bidder must be an officially certified partner for the installation, commissioning and maintenance of the specified equipment. Submit the equipment manufacturer's certificate or authorization as proof
4.7 | Delivery, assembly, adjustment, programming, testing and commissioning of the control unit of the IP intercom module for installation in the suspended ceiling in the halls of the complex with the following minimum characteristics: a) LAN interface: 2x RJ45 10/100T ports (auto-MDIX), Integrated 2- port LAN switch b) Power supply: PoE 802.3af (class 0 to 12.95W) or external power supply 9 to 36 V ± 10 % / 2 A DC c) Integrated 10W amplifier for external speaker d) Interfaces for connecting an external microphone e ) Two programmable active outputs - output current 600mA, with overvoltage and short-circuit protection f) Possibility of connecting external visual indicators, with programmable activation duration g) Two programmable, galvanically isolated inputs h) Minimum of three outputs for connecting programmable LED indicators i) Interface for connecting a 4x4 matrix keyboard or up to 16 independent external ones j) Multifunctional RESET button k) Realization of two-way communication l) Echo suppression - Acoustic Echo cancellation (AEC) m) Supported protocols: SIP 2.0, IPv4, ARP, TCP, UDP, DHCP n) Audio streaming (RTP, RTSP) o) Time synchronization (SNTP), p) Automatic configuration and firmware upgrade: TFTP r) Configuration via the web: HTTP/HTTPS s) The provider must be an officially certified partner for installation, commissioning operation and maintenance of the mentioned equipment. Submit the equipment manufacturer's certificate or authorization as proof
4.8 | Delivery, assembly, adjustment, programming, testing and commissioning of the indoor unit - IP anti-vandal intercom panel with the following characteristics: Physical characteristics: a) Anti-vandal housing - tested and certified according to EN 50486 standard, with IP69 degree of protection in accordance with EN 60529 standards and DIN 40 050-9, and mechanical protection IK10 in accordance with standards EN 62262 and EN 60068. Attach certificates as proof of compliance with the mentioned standards b) 2 integrated microphones with the ability to suppress background noise c) Integrated 10W speaker d) Two stainless, anti-vandal buttons (INFO and SOS) with clearly visible background lighting in different colors, the buttons are integrated in the case without screws e) Mounting the case in the wall - all additional equipment for placing in the wall must be included in the price f) With included cables of at least 2m for connection with control unit - minimum 2 cables JH(St)H 5x2x0.8 mm per unit Supported functionalities: g) Automatic detection and suppression of echoes and noises h) Automatic detection and alarm activation if the noise level exceeds the defined reference value (in dB) i) Graphic display of signal level history (Noise level graph) j) Auto-answer option - automatic answer to incoming calls without pressing a button k) Automatic audio test - Periodic testing of audio signals on the microphone and speaker to detect irregularities or interference l) Adaptive sound mode - automatic sound level adjustment depending on the noise level in the intercom environment m) Speech Transmission Index (STI) minimum 0.75 n) Supported speech codecs: G.711, G.729, G.722, L16/16kHz o) The bidder must be an officially certified partner for the installation, commissioning and maintenance of the mentioned equipment. Submit the equipment manufacturer's certificate or authorization as proof
4.10 | Delivery, installation and commissioning of IP announcement consoles with a microphone of the notification system with the following characteristics: a) Minimum of 12 customizable buttons with the possibility of broadcasting content in 12 different zones b) Support for SIP calls, SIP VoIP notifications, pre-prepared voice content and multicast notifications c ) Activity/status display on the buttons d) 2 x galvanically isolated logic inputs e 1 x galvanically isolated relay output, NO and NC contacts, maximum load 48V, 1A f) 2 x built-in stereo speakers, output power 2x1W g) 1 x microphone, symmetrical, XLR h) PoE power supply according to the 802.3af standard i) Headphone connection, jack 3.5mm j) Supported audio codecs: G.711 (PCMA, PCMU)/8 kHz, G.722
4.11 | Delivery, installation, setup, programming, testing and commissioning of the IP audio decoder of the notification system with the following minimum characteristics: a) Integration with the IP communication system - SIP support for integration with IP/SIP exchange or peer-to-peer b) Minimum 1x 10 /100TX (RJ45) port c) SD slot with support for microSD/microSDHC/microSDXC cards d) Minimum 1x 2-pin connector for connecting an external speaker e) Maximum output power 6W with PoE class 3 and 15W with PoE class 4 f) Nominal Speaker impedance- 4 – 16 Ω g) PoE power supply (802.3af and 802.3at) h) Minimum 1x 4-pin terminal block for two configurable inputs/outputs i) Control button for testing speaker impedance j) Built-in audio synchronization for speakers k) Minimum 512 MB RAM and 512 MB flash memory l) MP3 bandwidth: 64kb/s to 320kb/sm) Minimum operating temperature range from -20 °C to 50 °C n) Designed for 24/7 operation

## 5-Radio communication system
5 | Two-way radio communication system
RB | Description of technical requirements | Manufacturer | Model
5.1 | Digital Mobile Base Radio (DMR) with the following minimum characteristics:a.1) VHF frequency range 136-174 MHz a.2) Channel capacity: minimum 64 a.3) RF output power: in the range of 1 to 50 W a.4) AC power supply: input voltage 100-240 Vac, 47 -63 Hz, current consumption 0.9 A in broadcast mode (Tx) a.5) DC power supply: input voltage 11 -14.4 Vdc, current consumption 9.5 A in broadcast mode (Tx) a.6) Operating temperature: in the minimum range of - 30°C to +60°C a.7) Receiving antenna connector: BNC type female a.8) Transmitting antenna connector: N type female a.9) Minimum 2 Ethernet RJ-45 ports a.10) Minimum one DB25 type female (AUX) port a.11) For mounting in a 19" rack Receiver characteristics: b.1) Frequency range 136-174 MHz b.2) Channel spacing: 12.5 / 20 / 25 kHz b.3) Selectivity 12.5/20/ 25 kHz: 63/70/70 dB b.4) Digital sensitivity for 5% BER: 0.22 uV b.5) Intermodulation attenuation: 82/73 dB b.6) Audio distortion: less than 1%
Characteristics of the transmitter: c.1) Frequency range 136-174 MHz c.2) Transmitting RF power: in the range of 1 to 50 W continuously c.3) Frequency stability (at variation of temperature and supply voltage): 0.5 ppm c.4) Intermodulation attenuation: 40 dB c.5) Nominal deviation 12.5/20/25 kHz: ±5 kHz / ±2.5 kHz c.6) Modulation accuracy (4FSK): FSK error 5%, FSK Magnitude 1% c. 7) Audio distortions: less than 1% c.8) Digital vocoder type: AMBE +2tm vocoder
5.2 | VHF duplexer with the following minimum characteristics: a) With a minimum of 6 cavities 40x40mm equipped with silver-plated spiral resonators with a minimum diameter of 19mm b) Receiving/transmitting frequency: in the range of 136 to 175 MHz c) Maximum input power: 100 W at 1 dB of input attenuation d) Nominal impedance: 50 Ω e) Operating temperature: in the minimum range from -30° C to +60° C f) Frequency stability (with temperature variation): 8 ppm/° C g) Antenna connectors: N type female
5.3 | A VHF omni-directional antenna with the following minimum characteristics: a) Antenna construction made of hot-dip galvanized steel. All stainless steel fixing screws and nuts b) All metal antenna parts and fixing equipment are grounded c) VHF frequency range: 146-165 MHz d) Antenna gain: 2.2 dBi e) Impedance: 50 Ω f) Antenna polarization: vertical g) Maximum wind gust: 160 km/h) Connector type: N type female
5.6 | DMR handheld radio station without display with the following minimum characteristics:a.1) With included accelerometer for the "Man down" option a.2) Integrated Bluetooth module a.3) Integrated Wi-Fi module a.4) Location tracking inside the facility a.5) VHF frequency range 136-174 MHz a. 6) Channel capacity: minimum 64 a.7) Channel spacing: 12.5 kHz / 20 kHz / 25 kHz a.8) Max Dimensions with battery (H x W x D): 132 x 56 x 31 mm a.9) Max mass : 289g a.10) IP68 degree of protection against water immersion for 2m, 2 hours, and IP66 against high-pressure jet in accordance with IEC 60529 standard a.11) Operating temperature in the minimum range from -30 °C to +60 °C Characteristics transmitter: b.1) RF output power: 1W and 5W b.2) Digital modulation 4FSK b.3) Digital protocol: ETSI TS 102 361-1, -2, -3, -4 b.4) Frequency stability (at to variation of temperature and supply voltage): ±0.5 ppm b.5) Audio distortion: ≤1.5% b.6) Power on adjacent channel: 60 dB (12.5 kHz); 70 dB (20/25 kHz) b.7) Parasitic radiation: -36 dBm < 1GHz, -30 dBm > 1 GHz
Receiver characteristics: c.1) Analog sensitivity (12dB SINAD): 0.16 uV c.2) Digital sensitivity (5% BER): 0.14 uV c.3) Intermodulation: 70dB c.4) Selectivity: 60 dB (12.5 kHz); 70 dB (20/25 kHz) GNSS (Global Navigation Satellite System) features: d.1) Support for GPS and GLONASS d.2) Time to first fix TTFF, cold start: < 60 s d.3) Time to first fix TTFF, hot start: < 10 s d.4) Horizontal accuracy: < 5 m Bluetooth features: e.1) Version / range: 5.2 / Class 2, 10 meters e.2) Number of simultaneous connections: 1 audio accessory and 4 data device Wi-Fi characteristics: f.1) Supported standards: Wi-Fi 5 / IEEE 802.11a/b/g/n/ac f.2) Security protocols: WPA-3, WPA-2 f.3) Maximum SSID: 64
5.7 | DMR handheld radio station with a display with the following minimum characteristics:a.1) With integrated accelerometer for "Man down" option a.2) Integrated Bluetooth module a.3) Integrated Wi-Fi module a.4) Location tracking inside the facility a.5) VHF frequency range 136-174 MHz a. 6) Channel capacity: minimum 1000 a.7) Channel spacing: 12.5 kHz / 20 kHz / 25 kHz a.8) Max Dimensions with battery (H x W x D): 132 x 56 x 35 mm a.9) Max mass : 316 g a.10) IP68 degree of protection against water immersion for 2m, 2 hours, and IP66 against high-pressure jet in accordance with IEC 60529 standard a.11) Operating temperature in the minimum range from -30 °C to +60 °C Transmitter characteristics: b.1) RF output power: 1W and 5W b.2) Digital modulation 4FSK b.3) Digital protocol: ETSI TS 102 361-1, -2, -3, -4 b.4) Frequency stability ( at variation of temperature and supply voltage): ±0.5 ppm b.5) Audio distortion: ≤1.5% b.6) Power on adjacent channel: 60 dB (12.5 kHz); 70 dB (20/25 kHz) b.7) Parasitic radiation: -36 dBm < 1GHz, -30 dBm > 1 GHz
Receiver characteristics: c.1) Analog sensitivity (12dB SINAD): 0.16 uV c.2) Digital sensitivity (5% BER): 0.14 uV c.3) Intermodulation attenuation: 70dB c.4) Parasitic radiation: -57 dBm c. 5) Adjacent channel suppression (selectivity): 60 dB (12.5 kHz); 70 dB (20/25 kHz) GNSS (Global Navigation Satellite System) features: d.1) Support for GPS and GLONASS d.2) Time to first fix TTFF (Time To First Fix) cold start: < 60 s d.3 ) Time to first fix TTFF (Time To First Fix) hot start: < 10 s d.4) Horizontal accuracy: < 5 m Bluetooth features: e.1) Version / range: 5.2 / Class 2, 10 meters e.2) Number of simultaneous connections: 1 audio accessory and 4 data devices Wi-Fi features: f.1) Supported standards: Wi-Fi 5 / IEEE 802.11a/b/g/n/ac f.2) Security protocols: WPA-3, WPA-2 f.3) Maximum SSID: 128
5.13 | Server dispatch application for centralized control and monitoring of all stations in the system with all included licenses for the following functionalities:a) Remote monitoring of all radio devices in the network b) Communication between dispatchers and remote radio stations c) Broadcast broadcasting, creation of groups and emergency calls using "shortcuts" d) Telemetry - monitoring and control of remote devices with the possibility of creating profiles for different devices e ) Notification of system events for calls, text messages or status changes with the possibility of generating reports f) options for recording and listening to conversations g) GPS tracking h) Internal positioning i) Graphical interface for system management with the possibility of displaying on a map, displaying recorded conversations, listening, monitoring etc. j) Licenses for all listed functionalities must be included in position k) Mandatory full compatibility and functionality with the Operation Center for the voice system of Radio communication in prisons, located in Belgrade.
5.14 | Dispatch console with the following minimum characteristics: a) Console with a screen with a minimum resolution of 1024 x 768 b) Screen diagonal of at least 15” c) Goose neck microphone d) Stereo speakers, each at least 10W, with two separate encoders for volume control e) Dual USB audio f) PTT (push to talk) button g) LAN ports: (2 x Gigabit ethernet) h) Handset module with integrated PTT button
Delivery, assembly, installation and commissioning
5.15 | A set of Bluetooth self-powered beacons. The price must be stated as a set. It should be taken into account that the optimal range is up to 15 meters and that the price is shown as a set, and that the price should include all necessary Beacon devices in order to have an optimal range in all closed spaces in the complex with accompanying equipment (cables, connectors).

## 6-CATV
6 | Cable television system
RB | Description of technical requirements | Manufacturer | Model
6.1 | The main IPTV streaming server for the distribution of IPTV TV/Radio services with the following minimum features:a) 19" rack mount or wall mounting; b) Equipped with a minimum of 16xDVB-S/S2 + 6xDVB-T/T2/C input demodulators c) Equipped with a minimum of 8x CI interface (PCMCIA); d) With a minimum of 16 x QAM or COFDM modulators in the full range; e) With an integrated SCR multiswitch; f) With a minimum of 2 x 1000 Base-T (RJ 45) Ethernet ports; g) With a minimum of 2x USB 2.0 connectors (for data transfer or additional memory ); h) Data transfer speed minimum 83 Mbit/s
i) TV multiplexing from all inputs to any output transponder in order to optimize the available bandwidth; j) TV multiplexing on CA modules in order to reduce the number of CAMs; k) Support for LCN (Logical Channel Numbering); l) Support for filtering services with the option to remove unwanted services or remove services in order to reduce data transmission speed; m) Possibility of measuring the output load in real time; n) With the included license package for IP-out functionality with support for a minimum of 100 IP-out services (TV and Radio); o) With included license package for IP-in functionality with support for minimum 96 SPTP or MPTS IP-in streams, max 950 Mbit
6.2 | Compact modulator with the following minimum characteristics: a) Minimum 4x HDMI inputs for receiving HDMI signals and conversion to IP using UDP / RTP protocol (Multicast/Unicast); b) HDCP support; c) Support for gigabit IP streaming (up to 64 x SPTS / 4x MPTS); d) Local or remote management via web server; e) Support for SNMP v2 f) Rack or wall mounting; d) Video coding MPEG-4 AVC / H.264;
6.11 | Smart television with a screen diagonal of 43" 4K UHD with the following minimum characteristics: a) LED display with a diagonal of at least 43", resolution at least 3840 x 2160 b) Video characteristics: Viewing angle H/V: Minimum 178/178 Contrast Enhancer UHD Dimming Auto Motion Plus PQI ( Picture Quality Index): 2200 c) Audio characteristics; Sound Output (RMS): minimum 20W Supported Bluetooth audio Speaker type: 2CH e) VESA 200x200mm f) Digital broadcasting: DVB-T2 g) Built-in analog tuner h) Data broadcasting HbbTV 2.0.2 i) Connections: Minimum 2x USB, Ethernet LAN connection, WiFi5 supported, Minimum 1x RJ12, RF input j) Power supply: AC220-240V 50/60Hz k) Energy efficiency: class 4

## 7-CCTV
7 | Video surveillance system
RB | Description of technical requirements | Manufacturer | Model
7.1 | server with the following equipment and minimum features:
a) Housing: max. 2U for mounting in a rack b) Processor: min. 2x Intel Xeon Silver third generation, min. 8C/16T or better c) Memory: min. 4x 32GB RDIMM 3200MT/s Dual Rank or better d) Disk configuration: 12x 3.5" drives on the front of the server (SATA/SAS) e) RAID controller: min. RAID levels: 0, 1, 5, 6, 10, 50, 60; with back-up battery, min. 8GB cache f) Hard drives: 12x 3.5" SAS HDD, capacity min. 4TB, speed 7,200 rpm, connections 12Gbps g) Boot controller: controller card with support for 2 pieces of M.2 NVMe modules for RAID level 1 configuration (RAID1) h) Boot disks: min. 2x 240GB M.2 NVMe i) Network adapters: min. 2x 32GB FC Hot Buss Adapter j) Interfaces on the front: min 1x management port via micro USB port, 1x USB and 1x VGA k) Interfaces on the back: 2x USB, 1x VGA, 2x 1GbE BaseT (of which one port is used for server management) l) PCI slots: min. 3x 16 PCIe Gen4 m) Power supply: min. 1100W redundant power supply, class Titanium n) Rails: with the server it is necessary to deliver rails for mounting the server in the rack o) Front cover: with the server it is necessary to deliver a front cover (Bezel) that matches the server p) Server management: Within the server it is necessary deliver server management software without the need to install an additional server agent. Management of multiple servers at once through one interface without installing an additional server is supported. Support for locking server configuration and firmware for security and to prevent changes. Securely erase the contents of all drives supported. q) Additional functionalities: As part of the server, a module is also required that supports server communication with mobile devices (supported operating systems on mobile devices: Android and iOS) using wireless or Bluetooth technology. The module must allow assigning an IP address, changing the password to access the main monitoring module, managing the server and changing the BIOS settings. Through the module, insight into the server's hardware and software inventory, operational status, network data and logs must be enabled. r) Warranty: min. 3-year manufacturer's warranty with next business day response, visible on the manufacturer's website by entering the serial number
7.2 | Software for controlling the viewing and recording of video material, compatible with the system implemented in UIKS, Milestone Corporate basic license + Milestone Corporate license for each individual camera in the system, the possibility of integration with security systems. Licenses for all listed individual cameras should be included in the price. The contractor is obliged to integrate the cameras into the existing software at the location, according to the user's request.
7.3 | Professional IP dome "day/night" camera in an anti-vandal housingfor external mountinghigh performance, 1080p30, IP66, IK10; iDNA; HDR; ROI; H.264, cloud services; embedded video analysis; auto varifocal lens 3-9mm in high resolution with the following characteristics: a) 1/2.8" CMOS HD sensor, resolution 1920 x 1080 pixels FullHD b) Video compression H.264 and M-JPEG c) multiple configurable H.264 and M- JPEG streams, with adjustable bandwidth and frame rate d) HD standards - compatibility with SMPTE 274M-2008 standard: resolution 1920x1080p e) lens 3 to 9 mm, automatic varifocal with IR correction, high resolution f) Sensitivity (3100 K, scene reflectivity 89%, 1/25, F1.4, 30 IRE): color 0.0075 lx, black and white 0.0011 lx g) Dynamic range min 120 dB WDR (HDR) h) automatic motorized zoom adjustment/ focal lengths with 1:1 pixel mapping i) protocols: IPv4, IPv6, UDP, TCP, HTTP, HTTPS, RTP/RTCP, IGMP V2/V3, ICMP, ICMPv6, RTSP, FTP, ARP, DHCP, SNTP, SNMP, 802.1 x, DNS, DNSv6, DDNS, SMTP, iSCSI, UPnP (SSDP), DiffServ (QoS), LLDP, SOAP, Dropbox, CHAP j) Data encryption: TLS 1.2, SSL, DES, 3DES k) video motion analysis: Essential Video Analytics (Line crossing, Enter / leave field, Follow route, Loitering, Idle / removed object, Counting, Crowd density estimation, 3D tracking) l) Audio Full duplex / half duplex; 1 x audio input, 1 x audio output; audio alarm m) 2 alarm inputs, 1 alarm output n) supports direct iSCSI recording; SD memory card recording: continuous, alarm/event/scheduled recording, Internal RAM 60s pre-alarm recording
o) power supply: 12 VDC ±10%, Power-over-Ethernet 48 VDC nominal IEEE 802.3af (802.3at Type 1). Possible simultaneous power supply. p) operating temperature range: -30 ºC to +55 ºC q) casing in protection IP66, NEMA-4X and IK10 r) The bidder must be authorized by the equipment manufacturer for the sale, installation, commissioning and provision of service support of the offered equipment. Submit the authorization of the equipment manufacturer, which proves that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered video surveillance system equipment for the territory of the Republic of Serbia.
delivery, installation, connection, settings
7.4 | Procurement, delivery, installation, connection of IP dome "day/night" camera for indoor installation, auto varifocal lens 3.2-10.5mm, H.265 "multistreaming", cloud services, intelligent video analysis in the camera itself, audio detection, 1080p, with with the following characteristics: a) 1/2.8‑inch CMOS sensor, resolution 1920 x 1080 pixels b) Video compression H.264 (ISO/IEC 14496-10); MJPEG, H.265/HEVC c) multiple configurable H.265, H.264 and M-JPEG streams, with adjustable bandwidth and frame rate d) lens 3.2 to 10.5 mm, auto varifocal (AVF) with IR correction, high resolution e) Sensitivity (measured according to IEC 62676 Part 5)): in color 0.0210 lx, black and white 0.0040 lx, with IR diodes 0 lx f) Dynamic range 144 dB WDR (105 db measured according to IEC 62676 Part 5) g) P- iris, motorized zoom/focus control h) Hybrid operating mode: possibility of simultaneous streaming via analog SMB connector i) USB 2.0 Type C port j) protocols: IPv4, IPv6, UDP, TCP, HTTP, HTTPS, RTP/RTCP, IGMP V2/V3, ICMP, ICMPv6, RTSP, FTP, ARP, DHCP, APIPA (Auto-IP, link local address), NTP (SNTP), SNMP (V1, MIBII), SNMP (V3, MIBII), 802.1x, EAP /TLS, DNS, DNSv6, DDNS, SMTP, iSCSI, UPnP (SSDP), DiffServ (QoS), LLDP, SOAP, CHAP k) Data encryption: TLS 1.2; AES 256; AES 128; TLS 1.3, local storage encryption XTS-AES, video authentication: MD5; SHA-1; SHA-256; Checksum l) video motion analysis: intelligent video analytics (object in the field; crossing the line; entering/exiting the field; wandering; route tracking; counting; busy; state change; similarity search; stopping or starting the movement of the object) m) Audio Full duplex / half duplex; 1 x audio input, 1 x audio output; audio alarm n) 1 alarm input, 1 alarm output
o) SD memory card recording: continuous, alarm/event/scheduled recording, Internal RAM 5s recording before alarm p) power supply: Power-over-Ethernet 48 VDC nominal IEEE 802.3af (802.3at Type 1) Class 3 q) IR illuminator, 850nm, visibility in the dark up to 45m, adjustable strength r) operating temperature range: -20 ºC to +50 ºC s) The bidder must be authorized by the equipment manufacturer to sell, install, put into operation and provide service support of the offered equipment. Submit the authorization of the equipment manufacturer, which proves that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered video surveillance system equipment for the territory of the Republic of Serbia.
7.5 | Supply, installation, connection of a high-performance IP "day/night" PTZ camera for outdoor mounting, 1080p, IP68, H.265, iSCSI, 30x optical zoom, with the following features: a) 1/2 in CMOS sensor, resolution 1937 x 1097 (2.12 MP) b) integrated silicone wiper c) video compression H.265, H.264 (ISO/IEC 14496), M-JPEG, JPEG; multiple configurable H.265 and H.264 streams d) ONVIF Profile S, ONVIF Profile G, ONVIF Profile T, ONVIF Profile M e) lens 6.6-198 mm with 30x optical magnification, digital magnification 30x f) Sensitivity (3100K, reflectivity 89 %, 1/30, F1.6, 30 IRE): color mode 0.0047 lx; black and white mode 0.0013 lx g) Day/Night filter: monochrome, color, automatic modes h) Dynamic range min. 120 dB HDR, measured according to IEC 62676 Part 5 106 dB i) "Defog": improves visibility in foggy conditions, or in scenes with extremely low contrast j) "Brushless" motor, integrated pan/tilt drive k) Pan 360° continuous, Tilt: 290°, speed to preset position: 120°/s, preset precision up to ± 0.05°; variable speed Pan: 0.2°/s – 120°/s, Tilt: 0.2°/s – 90°/sl) protocols: IPv4, IPv6, UDP, TCP, HTTP, HTTPS, RTP/RTCP, IGMP V2/V3, ICMP , ICMPv6, RTSP, FTP, ARP, DHCP, APIPA (Auto-IP, link local address), NTP(SNTP), SNMP (V1, V3, MIB-II), 802.1x, DNS, DNSv6, DDNS (DynDNS.org , selfHOST.de, noip.com), SMTP, iSCSI, UPnP (SSDP), DiffServ (QoS), LLDP, SOAP, Dropbox™, CHAP m) Data encryption: TLS 1.0, TLS 1.1, TLS 1.2, DES, 3DES, AES, SSL
n) video motion analysis: Intelligent video analysis (IVA) - reliable detection and analysis of objects in the frame while suppressing unwanted alarms caused by different sources in the frame. Intelligent video analysis allows the camera to detect different behavior patterns of objects in the frame including left or removed objects, wandering, crossing multiple lines, people counting o) integrated sensors for monitoring internal temperature, air humidity, incoming voltage level, vibration p) masking: minimum 30 individually adjustable privacy masks; 256 pre-positions q) Operating temperature range: -40°S to 65°S r) Power supply: possibility of dual power supply, 24 VAC, 50/60 Hz and/or High PoE, 56VDC s) Built-in overvoltage protection on power connectors and mains connection t) Camera housing for outdoor installation - IEC 60529 IP66/IP68/Type 6P, IK10 (IEC 62262) degree of protection (except for glass) u) Permissible air humidity range: 0-100% w) Vibration resistance according to IEC 60068-2-6 x) Impact resistance according to IEC 60068-2-27 y) Corrosion test according to ISO 12944-6 C5-M (aluminum housing components) z) Power supply with transformer in a separate housing IP66, IK08 230VAC aa) Bidder must be authorized by the equipment manufacturer to sell, install, commission and provide service support for the offered equipment. Submit the authorization of the equipment manufacturer, which proves that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered video surveillance system equipment for the territory of the Republic of Serbia.
7.9 | Workstation for monitoring the video surveillance system:
a) Housing: Tower, or suitable b) Power supply: min. 750W c) Processor: min. Intel Xeon W3-2435, 8 cores with a base frequency of 3.1 GHz, 22.5 MB of cache memory or equivalent with the same or better characteristics d) Chipset: min. Intel PCH W790 or equivalent with the same or better characteristics e) RAM memory: min. 1x 16GB DDR5 4800MHz, with additional 7 free memory slots, maximum expandability up to min. 1TB f) Hard disk: min. 512GB SSD M.2 NVMe g) Graphics card: min. 16GB GDDR6, 256-bit, 4x Display port, support for simultaneous connection of 4 displays with a resolution of 5120x2880pxl at a frequency of 60Hz h) Ports on the front: min. 2x USB 3.2 Gen 1, 2x USB 3.2 Gen 2 Type-C, and 1x audio port i) Rear ports: min 3x USB 3.2 Gen 2 Type-C, 3x USB 3.2 Gen 1, 1x RJ45 1GBE Ethernet and 1x RJ45 10GBE Ethernet j) Expansion slots: min. 2x 2.5/3.5 inch HDD/SSD SATA, 1x Full-height Gen5 PCIe x16, 1x Full-height Gen4 PCIe x16, 2x Full-height Gen4 PCIe x8 and 1x Full-height Gen4 PCIe x8 k) Protection: TPM 2.0. BIOS integrity check against manufacturer's cloud backup. Checking within the same host is not allowed. l) Automatic performance optimization of selected applications based on self-learning and artificial intelligence routines. m) Automatic sound optimization, reduction of background noise on the part of participants and interlocutors during conference calls. n) Peripherals: USB keyboard and mouse included, from the same equipment manufacturer as the workstation o) Operating system: min. Windows 11 Pro p) Warranty: min. 36-month manufacturer's warranty, verifiable on the manufacturer's website
7.10 | small monitor for monitoring a video surveillance system with the following minimum features:a) Diagonal: min. 23.8 inches b) Panel type: IPS (In-Plane Switching Technology) Anti-Glare c) Resolution: min. FullHD 1920x1080px d) Lighting: min. 250 cd/m² e) Screen response: max. 5ms (grey-to-grey) f) Contrast: 1000:1 g) Viewing angle: 178°/178° h) Ports: minimum 1h DisplayPort 1.2 (with HDCP support), 1h HDMI 1.4 (with HDCP support), 1x VGA, 1x USB 3.2 Gen1 (upstream) and 4x USB 3.2 Gen1 i) Mobility: Height adjustable (up to 150mm) j) Tilt (-5° to 21°) k) Vertical rotation: Pivot (-90° to 90°) ) l) Horizontal rotation: Swivel(-45° to 45°), m) Advanced functions: Hardware filter that reduces the emission of blue light, without affecting the accuracy of color display. n) It is necessary that the monitor is from the same manufacturer as the computer (Workstation for monitoring the video surveillance system) o) Cables: It is necessary that the monitor is supplied with a voltage cable and a DisplayPort cable for connection to the workstation p) Warranty: min. 36-month manufacturer's warranty, verifiable on the manufacturer's website
7.11 | Monitor for monitoring the video surveillance system: a) Diagonal: min. 49.5 inches b) Operating mode: Intended for 24/7 operation c) Resolution: min. 3840x2160, Antiglare d) Panel type: VA or equivalent e) Aspect ratio: 16:9 f) Response: max. 10ms d) Contrast: static, min. 5000:1 h) Illumination: min. 500 cd/m² i) Viewing angle: 178°/178° j) Screen frame thickness: max. 15mm all edges of the screen k) Housing: metal l) Screen orientation: Ability to work in vertical and horizontal orientation m) MTBF parameter: min. 50,000 hours Ports: n) Input AV signal: min 3x HDMI, 1x DisplayPort ,1x VGA, 1x audio 3.5mm o) Output AV signal: min 1x DisplayPort (DaisyChain), 1x audio 3.5mm p) For screen control: min 1x RS -232c, 1x IR (3.5mm stereo mini) and 1x RJ45 LAN. CPU: A73*4+A53*4, GPU: G52 MP8 u) Memory: min 4GB v) Data storage: min: 32GB
a) Operating system: Android 11 OS or similar b) Advanced functionalities: HDCP, Plug&Play system, Anti image retention functionality, Media playback functionality, functionality of detecting a non-existent signal at the current input (Input) and automatic reproduction of the next input signal according to the defined list of priorities, support for Security Lock c) VESA: 400 x 400 d) Cables: It is necessary to supply the screen with a voltage cable, HDMI cable, RS-232c cable, as well as a remote control with batteries e) Bracket: Bracket for mounting on the wall with a capacity that corresponds to the weight of the monitor and with the possibility of adjustment in all 3 axes f) Warranty: min. 36 months manufacturer's warranty

## 8-ACC
8 | Access and movement control systems and panic buttons
RB | Description of technical requirements | Manufacturer | Model
8.1 | An intelligent modular controller for an access control system with the following features:a) physical connection of up to 4 card readers via the Wiegand communication interface b) reader power supply directly from the controller c) 8 supervised analog inputs that can be used as digital or analog contact d) 8 relay outputs that can work in Dry (without potential) or Wet (maximum 30 VDC and 1.25 A) operating mode e) Ethernet 10/100BaseT RJ45 and RS485 port for connection with the server f) local buffer memory compact flash min. 2 GB g) independent access processing, authorization, opening/closing control and pass registration in offline mode h) tamper switch i) LCD display for displaying information j) support for expansion with an additional module for access control up to a total of 8 card readers k) support for additional expansion modules up to 16 alarm inputs and 16 relay outputs l) operating temperature range: 0°C to +50°C m) supplied complete with a housing with 2 DIN rails n) supplied complete with a 60W power supply with with overvoltage protection and an integrated device for charging batteries with LED status indicators and a temperature sensor. necessary licenses for integration into the existing system. The bidder must be authorized by the equipment manufacturer to sell, install, put into operation and provide service support for the offered equipment. Submit the authorization of the equipment manufacturer proving that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered access control system equipment for the territory of the Republic of Serbia.
8.2 | Access control controller expansion module with additional 4 card readers with the following features:a) physical connection of up to an additional 4 card readers via the Wiegand communication interface b) reader power supply directly from the controller expansion module c) additional 8 monitored analog inputs that can be used as digital or analog contact d) additional 8 relay outputs that can to work in Dry (no potential) or Wet (maximum 30 VDC and 1.25 A) operating mode e) RS485 connection with the controller f) tamper g) operating temperature range: 0°C to +45°C h) mounted on rail in a suitable housing. i) supplied complete with a 60W power supply with surge protection and an integrated battery charger with LED status indicators and a temperature sensor. The bidder must be authorized by the equipment manufacturer to sell, install, commission and provide service support for the offered equipment. Submit the authorization of the equipment manufacturer proving that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered access control system equipment for the territory of the Republic of Serbia.
8.3 | Contactless access control reader with the following features: a) reads iClass, Mifare and Mifare Desfire EV1 cards, b) works at a frequency of 13.56 Mhz c) card reading distance up to 7.6 cm d) supports 32-bit format in accordance with ISO standard 14443A e) multi-colored status LED diode g) connects to the controller via the Wiegand interface, h) IP 55 protection category, i) operating temperature range: -35°C to + 65°C j) black color, for wall mounting The bidder must be authorized by the equipment manufacturer for the sale, installation, commissioning and provision of service support of the offered equipment. Submit the authorization of the equipment manufacturer proving that the bidder is an authorized partner for the sale, installation, commissioning and provision of service support for the offered access control system equipment for the territory of the Republic of Serbia.

## 9-Attack
9 | Anti-sabotage systems
RB | Description of technical requirements | Manufacturer | Model
9.1 | Device for detecting mobile phones with static magnetic technology:Magnetic-static detector - mobile phone detector • The device must be new, unused; • The system must be fully integrated in one piece and must not require any type of assembly for independent operation after transport; • Weight: The complete detector must not weigh more than 10 kg; • The system must have IP65 protection, without additional covers; • The system must not have protrusions, any buttons, keys or other parts in the path of passage; • The system must provide a digital display and interface that offers at least two password-protected levels of user access; • The system must be able to enable remote Bluetooth signaling when operating in that mode; • The system must have legs for fixing on smooth floor surfaces; • The system must have a collapsible transport case that takes up minimal space when the detector is in use. Equipment and accessories must fit in the footbed and the total weight of the complete set must not exceed 13 kg; • The system must have at least 5 different zones for alarm height indication; • The system must always provide an audible alarm indication when detecting ferromagnetic objects • The system must have an audible alarm signal that must provide an alarm indication that has a proportional tone • The system must have an integrated power source capable of charging the Ni-MH batteries located inside the device; • The system must provide continuous operation time of at least 24 hours after fully charging the battery;
9.2 | Metal detector door Metal detector door (MDV) with the following characteristics: • MDV must be compatible with the system implemented in UIKS; CEIA NetID + CEIA NetID license. • The device must be new, unused; • Required MDVs must use the latest technological (improved) solutions and have very high uniformity in hazard detection throughout the transit area, ultra high discrimination of personal metal objects of people passing through the door to ensure high throughput. • MDVs must detect all types of metal weapons and/or metal dangerous objects (magnetic and non-magnetic) regardless of the position and speed of passing through the door of the person being controlled; • they must have the ability to detect in the entire transit area and discriminate metal objects in visitors and persons being controlled; • uniform detection field and a minimum of 40 different detection zones; • two visual displays (LED BARS) in both directions (input and output), along the entire height of the antenna, where it will show the height of the detected object; • sound and visual signal during metal detection; • complete resistance to external mechanical and electrical influences, as well as security of detection in accordance with the chosen parameters and the chosen security standard; • the ability to adjust detection in accordance with the international security standard NIJ-0601.02; • the detector must provide an alarm indication for each test sample determined by the NIJ-0601.02 standard (Lo – size of large object, Mo – size of medium object, So – size of small object) • high level of detection with the possibility of programming, ie. additional setting of the detection level, in accordance with the needs of the end user (local or remote), namely: MDV programming must be protected by mechanical protection and a code, especially for operators and especially for supervisors • programming must be possible in one of the following ways: using the keyboard on to the MDV control panel itself, programming with the help of the RS232 port, with the help of a chip card with predefined standards of sensitivity (it has a card slot) and detection, infrared (IR) remote programming protected by a code; and via bluetooth • MDVs must have internal batteries for operation in the event of a power outage; • MDVs must have an automatic daily testing procedure with associated accessories, the result of which will be immediately displayed on the control unit; • with the MDV, the supplier must deliver a set of equipment with which the daily functionality test of the device is performed;
• it is necessary that the display shows the type of metal object detected (magnetic or non-magnetic) and that this function can be activated/deactivated through advanced programming by the supervisor; • it is necessary that the visual display shows the selected safety standard every time the MDV is put into operation; • MDVs must have the option of self-diagnosis and immediate failure signaling at the start of operation, as well as during operation; • MDVs must not require additional daily calibration; • MDVs must have the Random alarm option; The passing of persons who do not activate the alarm, i.e. do not possess dangerous objects, but the alarm in the given required range will still be activated by a special audio-visual signal, in order to control the operator and the safety level of the objects) • the detector must have a magneto-static detector for detecting standard and miniature mobile and smart phones • optical and acoustic signaling is necessary for this function, which facilitates the secondary inspection performed by operators • the possibility of automatic synchronization between two or more MDVs, at a distance of up to 5 cm, without the use of external cables; • power supply 230 V, +/- 10%, 47-63 Hz, 40VA typical consumption • working temperature min: from 0°C to 40°C; • air humidity: 0 to 95% without condensation;