## Sheet1
Vendor list with proof of fulfilment of conditions
No | Description of technical requirements | Manufacturer | Model
74. | Enterprise Server / BMS software. The Enterprise Server is a software-based server that collects site-wide data for aggregation and archiving, yet is flexible enough to run stand-alone applications. The Enterprise Server also serves as a single point of administration through WorkStation or WebStation.
75. | StruxureWare building operation workstation/ BMS workstation. Operation is a fully featured environment for operating and administering all aspects of the software. WorkStation is the window through which users can monitor their energy usage and continuously improve their building’s efficiency
SmartX IP-IO series, IP-IO-DI10: 10 Digital Inputs
SmartX IP-IO series, IP-IO-UIO5DOFA4: - 5 Universal I/O (type b), 3 2A Form A Relays, 1 12A (HP) Form A Relay
SmartX IP-IO series, IP-IO-DI10: 10 Digital Inputs
SmartX IP-IO series, IP-IO-UIO5DOFA4: - 5 Universal I/O (type b), 3 2A Form A Relays, 1 12A (HP) Form A Relay
SmartX IP-IO series, IP-IO-DI10: 10 Digital Inputs
SmartX IP-IO series, IP-IO-UIO5DOFA4: - 5 Universal I/O (type b), 3 2A Form A Relays, 1 12A (HP) Form A Relay
Power supply 24VAC/VDC (PS-24V) Smart power supply for automation controllers up to 30W. LED status. Installation on a din rail over a base.
Universal base for mounting on a DIN rail, for a power supply module
Automation Server Premium (AS-P) - Communication protocols (BacNET, LON, Modbus) - Communication ports (Ethernet, LonWorks, USB host, USB device, 2 x RS-485) - CPU (frequency 160 MHz, SDRAM 128 MB, flash memory 4 GB) Support for HHTP/HTTPS, SMTP, NTP, DHCP, IP addressing. Supported WEB services. RS-485 communication with automation modules, power supply via Smart power bus (7 W, 24 VDC), installation on DIN rail via base. Control of up to 30 automation modules.
Universal base for mounting on a DIN rail, for the premium automation server / controller
Module I/O 16DI – Digital In (DI-16) - digital input (minimum pulse width 120 ms) - counter input (minimum pulse width 20 ms, maximum frequency 25 Hz) 16 digital inputs. Voltage-free contacts, 24 VDC, 2.4 mA, RS-485 communication with automation server, power supply via internal bus from Smart power supply (1.6 W, 24 VDC), installation on DIN rail via base, HOT SWAP option enabled (change of IO module while under power supply
Module I/O 12DO – Digital Output FormA (DO-FA-12) - digital outputs (contacts: 250 VAC/30 VDC, 2A, minimum pulse width 100 ms, Form A, 12 NO) 12 digital outputs. RS-485 communication with automation server, power supply via internal bus with Smart power supply (1.8 W, 24 VDC), installation on DIN rail via base.
Module I/O 16UI – Universal In (UI-16) - digital input (24 VDC, 2.4 mA, voltage-free contacts, minimum pulse width 120 ms) - counter input (24 VDC, 2.4 mA, voltage-free contacts, minimum pulse width 20 ms , maximum frequency 25 Hz) - voltage input (0-10 VDC, accuracy +/- 7mV) - current input (0-20 mA, accuracy +/- 0.03 mA) - resistance input (10Ω to 10kΩ or 10kΩ to 60kΩ) - temperature input (-50°C to 50°C) 16 universal inputs. RS-485 communication with automation server, power supply via internal bus with Smart power supply (1.8 W, 24 VDC), installation on DIN rail via base
Module I/O 8AO - Analog Out Voltage (AO-V-8) 8 analog outputs. -1mA to 2 mA, 0-10 VDC, RS-485 communication with automation server, power supply via Smart power bus (0.7 W, 24 VDC), installation on DIN rail via base
Universal base for mounting on a DIN rail, for I/O module
Power supply 24VAC/VDC (PS-24V) Smart power supply for automation controllers up to 30W. LED status. Installation on a din rail over a base.
Universal base for mounting on a DIN rail, for a power supply module
Automation Server Premium (AS-P) - Communication protocols (BacNET, LON, Modbus) - Communication ports (Ethernet, LonWorks, USB host, USB device, 2 x RS-485) - CPU (frequency 160 MHz, SDRAM 128 MB, flash memory 4 GB) Support for HHTP/HTTPS, SMTP, NTP, DHCP, IP addressing. Supported WEB services. RS-485 communication with automation modules, power supply via Smart power bus (7 W, 24 VDC), installation on DIN rail via base. Control of up to 30 automation modules.
Universal base for mounting on a DIN rail, for the premium automation server / controller
Module I/O 16DI – Digital In (DI-16) - digital input (minimum pulse width 120 ms) - counter input (minimum pulse width 20 ms, maximum frequency 25 Hz) 16 digital inputs. Voltage-free contacts, 24 VDC, 2.4 mA, RS-485 communication with automation server, power supply via internal bus from Smart power supply (1.6 W, 24 VDC), installation on DIN rail via base, HOT SWAP option enabled (change of IO module while under power supply
Module I/O 12DO – Digital Output FormA (DO-FA-12) - digital outputs (contacts: 250 VAC/30 VDC, 2A, minimum pulse width 100 ms, Form A, 12 NO) 12 digital outputs. RS-485 communication with automation server, power supply via internal bus with Smart power supply (1.8 W, 24 VDC), installation on DIN rail via base.
UPS-UNINTERRUPTED POWER SUPPLY
Rack UPS for installation in telecommunications cabinets, 8kVA, 230V, 50Hz, with the following characteristics:
Output
Maximum output power: 8.0kW / 8.0kVA
Output frequency: 50/60Hz +/- 3 Hz, nominal
Topology: online, double voltage conversion, output voltage shape: pure sinusoid
Output voltage distortion: less than 2%
Time to switch to battery mode and vice versa: instant
Output connections: 6 x IEC 320 C13, 4 x IEC 320 C19, 1 x Hard Wire 3-wire output-single-phase (UPS mode of operation).
The possibility of forming a "switched outlet" group" that enables power management of devices connected to the UPS (sequential restart, switching on, off, ...)
Built-in ByPass (automatic and manual)
Automatic restart of the power supply after the arrival of electricity in the city grid,
Nominal output voltage: 230V. Other possible voltages: 220V, 240V
Input
Nominal input voltage: 230V, 220, 240, 380, 415V
Input voltage range for normal operation: 176 - 275 VAC, at 50% load 100 - 275 VAC, or 173 - 476 (3-phase connection))
Input frequency: 40 - 70 Hz (automatic)
Type of input connection: "hard-wire", single-phase or 3-phase connection possible
Batteries
Battery type: Lead-acid sealed battery, maintenance-free, with suspended electrolyte
Average battery life: 3-5 years
Typical charge/discharge time: 1.5 h
Simple battery replacement, without the need to go to the service centre. Possible replacement of the battery pack on "hot" ("Hot-Swap")
The possibility of extending the autonomy with additional external battery packs, up to a total of 10 battery packs, while the charging and discharging time does not change
Autonomy: 7.5 minutes at 6.4kW load / 14.5 minutes at 4kW load
Communication and management
Communication port: RJ45-serial, USB, Network card with temperature probe and one optional ("NC" model only). Communication software is supplied with the device.
Control panel: Multi-function LCD screen with navigation keys for managing UPS resources. Apart from device status information (battery status, load size, consumption of
electricity,..), possible predicative date of internal battery replacement. Navigation keys enable menu selection, as well as UPS parameter setting.
EPO connection
Audio alarm.
Surge protection and filtering
Degree of protection: 480 J
Physical features, guarantee
Height x width x depth: 432mm x 263mm x 715mm. The UPS is rack/tower convertible and with the addition of a rail-kit, it can be installed in a 19" rack and occupies 2U of height. With UPS marked "RM"
elements for mounting in a 19" rack are supplied. In the rack, it occupies 6U of height.
Weight: 111.82 kg
Operating temperature: 0 - 40 °C
Operating relative humidity: 0 - 95 %
Noise level at 1 m distance: 55.0 dBA
thermal dissipation: 1497.0 BTU/hr
Warranty: 3 years on hardware, 2 years on internal battery
option to extend the warranty period by +1 year with part no. WBEXTWAR1YR-SP-06, with a 4-year warranty on both hardware and batteries
option to extend the warranty period by +3 years with part no. WBEXTWAR3YR-SP-06, with a 6-year warranty on both hardware and batteries
RoHS compatible
Supported Standards/Approvals: CE, CE Mark, EAC, EN/IEC 62040-1, EN/IEC 62040-2, IRAM, RCM, VDE
TYPE: SRT8KRMXLI, APC or equivalent
A complete UPS, assembled, tested and functionally adjusted for smooth operation.